# Amesim Model of the M.Sc. Thesis: Solar-Assisted GSHP with PCM Storage

Oct 1, 2026 · @Hakan

## How to use this guide

This guide builds your M.Sc. thesis system in Simcenter Amesim exactly as the thesis calculates it: same equations, same hourly input data, same values and the same hour-by-hour control order. Built correctly, the model gives the thesis results: 10 821 kWh of condenser heat, 2 626 kWh of compressor work and 2 265 heat-pump hours.

The system is the one in Figure 3.1 of the thesis: a 40 m² tomato greenhouse in Bursa (18 °C), 30 m² of flat-plate solar collectors, a PCM store filled with CaCl₂·6H₂O, a 10 kW heat pump and a horizontal ground heat exchanger (6 modules × 95 m, 1 m deep). The season runs from 1 October 2013 to 31 March 2014.

The thesis is an hourly energy balance with an ideal store. So the exact replica of the thesis (Level A) is built mostly from Signal blocks, plus a small Thermal network that checks the greenhouse temperature. Level B, at the end, is an optional physical version with water loops and a real PCM store; it goes beyond the thesis, so its results will differ.

The input files are in the amesim/ folder of the GitHub project (greenhouse-solar-gshp-pcm.zip, sent in the chat):

| File | Content | Thesis source |
| --- | --- | --- |
| tout.data | Hourly outdoor air temperature (°C) | DMİGM data used in Eq. (3.1) |
| itilt.data | Hourly irradiance on the 35° collector plane (W/m²) | Figure 3.10 |
| cop.data | Monthly heat-pump COP | Table 3.7 |
| tsoil.data | Daily soil temperature at 1 m (°C) | Eq. (2.23), Figure 3.8 |
| evap_ratio_monthly.data | Monthly evaporator-to-condenser heat ratio (optional) | Table 3.7 enthalpies |
| expected_monthly_results.csv | Monthly results to compare with | Tables 4.2–4.7 |

Build in this order and run a one-day test after each step: inputs → heat demand and solar heat → PCM store → heat pump → ground check → greenhouse check and outputs.

Submodel names (the short IDs under each icon) differ between Amesim versions and licences. This guide names each component by its library and function. In Submodel mode, press Premier submodel first, then check each icon against the description here.

## Libraries and setup rules

Level A needs two standard libraries; Level B adds one more.

| Library | Used for |
| --- | --- |
| Signal, Control and Observers | Time tables, gains, sums, products, f(x) and f(x,y) expressions, relays, integrators |
| Thermal | Greenhouse check: temperature source, conductance, thermal capacity, heat flow source |
| Thermal-Hydraulic | Level B only: water loops, pipes, chambers, pumps, three-way valves |

Follow these rules everywhere:

- Units. Signals carry no units in Amesim. This guide uses W for power, J for energy, °C for temperature and s for time. Integrated energies are converted to kWh at the end with a gain of 1/3.6e6.

- Time tables. Use a time-table source that reads a 1D table file, with the simulation time as input. Set interpolation to linear and extrapolation to "hold last value". The files already hold each hourly value constant (a staircase), so linear interpolation reproduces the thesis hours.

- Time origin. t = 0 s is 1 October 2013, 00:00. The season ends at 15 724 800 s (182 days).

- Expressions. In the f(x) and f(x,y) blocks the inputs are called x and y; max, min, exp and cos are available. If your version has no f(x) block, build the same line from gain, sum, saturation and min/max blocks.

- Thermal causality. Connect capacity-type items (thermal capacity, temperature source) to flow-type items (conductance, heat flow source). Two flow-type items need a small thermal capacity between them.

- Heat flow sign. A positive heat flow source adds heat to the node it touches.

Tip: define the values of the next tables as global parameters (Settings → Global parameters), for example UA_GH = 448.078. Then a parameter field can hold the name, and every value has one home.

## System connection diagram

Solar heat goes to the greenhouse first, any surplus fills the PCM store, and the heat pump covers the rest with heat from the ground loop.

thesis system (Figure 3.1) as built in Level A · 3 heat sources in a fixed order

Each box is built in one step of this guide: the solar collectors and the greenhouse demand in Step 1, the store in Step 2, the heat pump and electricity in Step 3, the ground loop in Step 4 and the greenhouse check in Step 5.

## Global parameters (thesis values)

Every number in the model comes from the thesis. None of them is an assumption in Level A.

| Name | Meaning | Value | Unit | Thesis source |
| --- | --- | --- | --- | --- |
| UA_GH | Greenhouse loss coefficient, (A1/R1 + A2/R2)·f_w·f_c·f_s = (72.5 + 46.56)/0.26 × 1.03 × 1.00 × 0.95 | 448.078 | W/K | Eq. (3.1), Section 3.1.1 |
| T_SET | Greenhouse set point (tomato) | 18 | °C | Table 3.5 |
| K_SOL | Collector area × collector efficiency × system efficiency = 30 × 0.35 × 0.70 | 7.35 | m² | Eq. (3.6), Table 3.13 |
| COP | Monthly heat-pump COP, Oct → Mar | 5.28, 4.79, 4.07, 3.67, 3.92, 4.38 | – | Table 3.7 |
| R_EV | Evaporator heat / condenser heat, (h1 − h4)/(h2 − h3) for October = 148/172 | 0.8605 | – | used in Tables 4.2–4.7 |
| Q_HP | Heat-pump heating capacity | 10 000 | W | Section 3.4 |
| UA_GHX | Ground heat at design flow per K of (T_soil − 2 °C): n·m·c_p·[1 − exp(−k_t·F(z)·L / (m·c_p))] | 1181.96 | W/K | Eq. (2.24) |
| G_GHX | Same, at unlimited flow: n·k_t·F(z)·L = 6 × 2.42 × 1.052554 × 90 | 1375.48 | W/K | Eq. (2.24) |
| T_S1 | Water temperature at the ground-loop inlet | 2 | °C | Section 3.4 |
| m_mod | Water flow per ground-loop module, ρ·u·π·d_i²/4 with u = 0.5 m/s, d_i = 21.1 mm | 0.1748 | kg/s | Eq. (2.25) |
| T_m, T_0, D | Soil model: mean, amplitude, damping x·√(π/(a·P)) at 1 m | 17.12, 13.98, 0.3585 | °C, K, – | Eq. (2.23), Section 3.3 |
| PCM | CaCl₂·6H₂O: melting point, latent heat, density, volume, mass | 29 °C, 187 kJ/kg, 1710 kg/m³, 1.94 m³, 3317 kg | – | Section 3.6 |
| T_END | Season length, 1 Oct 2013 00:00 → 1 Apr 2014 00:00 | 15 724 800 | s | Chapter 3 |

The PCM values are used only in Level B. In Level A the store is ideal, as in the thesis: no size limit, no loss and perfect heat transfer.

## Inputs: weather, COP and soil tables

Four time tables feed Level A. They hold the exact hourly, daily and monthly values the thesis calculation used.

| Icon | Component (Signal library) | File | Output |
| --- | --- | --- | --- |
| TAB_TOUT | Time table source from a 1D table file | tout.data | T_out (°C) |
| TAB_IT | Same | itilt.data | I_T (W/m²) |
| TAB_COP | Same | cop.data | COP (–) |
| TAB_SOIL | Same | tsoil.data | T_soil at 1 m (°C) |

Each file starts with three comment lines; the first is # Table format: 1D. The data follow as two columns, time in seconds and value. Every interval has two points, at its start and one second before its end, so the value stays constant through the hour, day or month:

time_s,T_out_C
0,8.0
3599,8.0
3600,7.8
7199,7.8

If your Amesim version does not read a file, open it in the Table Editor, check that it shows two columns (x = time, y = value) and save it again in the native format.

The irradiance file is in W/m², and the thesis series is in Wh/m² per hour. These are the same number, because an hourly energy of 55.3 Wh/m² equals a mean power of 55.3 W/m² over that hour.

I checked the files before sending them. Integrated over the season they give the thesis energies: 16 748 kWh of heat demand and 5 941 kWh of useful solar heat.

## Step 1 – Heat demand and solar heat

This step turns the weather into two powers: the greenhouse heat demand (Eq. 3.1) and the useful solar heat (Eq. 3.6). It then splits the solar heat into the part used directly and the surplus.

Q_{dem} = \max\left[0,\; UA_{GH}\,(T_{set} - T_{out})\right] = \max\left[0,\; 448.078\,(18 - T_{out})\right]

Q_{fay} = A_c\,\eta_{kol}\,\eta_m\,I_T = 7.35\,I_T

Q_{dir} = \min(Q_{fay},\,Q_{dem}), \qquad Q_{ch} = Q_{fay} - Q_{dir}, \qquad Q_{def} = Q_{dem} - Q_{dir}

The thesis sets negative heat losses (outdoor air warmer than 18 °C) to zero demand; the max(0, …) does the same.

| Icon | Component (Signal library) | Setting | Output |
| --- | --- | --- | --- |
| F_DEM | f(x) expression, x = T_out from TAB_TOUT | max(0, 448.078*(18 - x)) | Q_dem (W) |
| G_SOL | Gain, input I_T from TAB_IT | 7.35 | Q_fay (W) |
| F_DIR | f(x,y) expression, x = Q_fay, y = Q_dem | min(x, y) | Q_dir (W), solar used directly |
| SUB_CH | Sum, inputs + Q_fay and − Q_dir | – | Q_ch (W), surplus to the store |
| SUB_DEF | Sum, inputs + Q_dem and − Q_dir | – | Q_def (W), deficit after direct solar |

Connections:

- TAB_TOUT → F_DEM

- TAB_IT → G_SOL

- G_SOL → F_DIR (x) and SUB_CH (+)

- F_DEM → F_DIR (y) and SUB_DEF (+)

- F_DIR → SUB_CH (−) and SUB_DEF (−)

Only one of Q_ch and Q_def can be above zero in any hour: either the sun covers the demand, or it does not.

Checks with the thesis worked examples:

- At t = 0 s (1 Oct 2013, 00:00, T_out = 8 °C), Q_dem = 4 481 W. Section 3.1.1 gives 4 480 W.

- At t = 25 200 s (1 Oct, 07:00, I_T = 55.3 W/m²), Q_fay = 407 W. Section 3.5 gives 404 W, with I_T rounded to 0.055 kWh/m².

## Step 2 – PCM store and the dispatch order

The store takes every solar surplus and gives it back when there is a deficit, before the heat pump starts. This is the thesis control order (Chapter 3): solar first, then the store, then the heat pump.

The store is ideal, as in the thesis: no size limit, no heat loss, perfect heat transfer. So it is an energy counter, not a temperature node:

\frac{dE}{dt} = Q_{ch} - Q_{dis}, \qquad E \ge 0, \qquad Q_{dis} = Q_{def}\cdot S_E, \qquad S_E = \begin{cases}1 & E > 0\\ 0 & E = 0\end{cases}

| Icon | Component (Signal library) | Setting | Output |
| --- | --- | --- | --- |
| SUM_E | Sum, inputs + Q_ch and − Q_dis | – | dE/dt (W) |
| INT_E | Integrator, with a lower limit if your version has one | initial value 0 J, lower limit 0 J, no upper limit | E (J), energy in the store |
| REL_E | Relay (on/off with hysteresis), input E | ON above 1000 J, OFF below 1 J; outputs 1 and 0 | S_E |
| MUL_DIS | Product, inputs Q_def and S_E | – | Q_dis (W), heat from the store |

Connections: SUB_CH → SUM_E (+); MUL_DIS → SUM_E (−); SUM_E → INT_E → REL_E; REL_E and SUB_DEF → MUL_DIS.

The relay threshold of 1 J keeps E from going below zero. If your integrator has no lower limit, E may dip a few joules below zero for one solver step; this is negligible.

What to expect with no size limit: E peaks at 3.906e8 J (108.5 kWh) at the end of the 16:00 hour of 17 October 2013 (t = 1 443 600 s) and ends the season at 13.3 kWh. The thesis states a peak of 150.3 kWh in Section 3.6.1; the published daily values of Tables 4.2–4.6 lead to 108.5 kWh. To try a real tank size, set the INT_E upper limit to the thesis design energy, 173 kWh = 6.228e8 J.

## Step 3 – Heat pump

The heat pump covers whatever the sun and the store cannot. Its COP changes by month only, as in Table 3.7 of the thesis.

Q_{cond} = Q_{def} - Q_{dis}, \qquad W = \frac{Q_{cond}}{\mathrm{COP}}, \qquad Q_{evap} = R_{EV}\,Q_{cond} = 0.8605\,Q_{cond}

| Icon | Component (Signal library) | Setting | Output |
| --- | --- | --- | --- |
| SUB_HP | Sum, inputs + Q_def and − Q_dis | – | Q_cond (W), condenser heat |
| DIV_W | Division, or f(x,y) = x/y with x = Q_cond, y = COP from TAB_COP | – | W (W), compressor electricity |
| G_EV | Gain, input Q_cond | 0.8605 | Q_evap (W), heat taken from the ground |
| CMP_HP | Comparator (or f(x) = x > 1), input Q_cond | 1 if Q_cond > 1 W, else 0 | HP_on |

Connections: SUB_DEF → SUB_HP (+); MUL_DIS → SUB_HP (−); SUB_HP → DIV_W (x), G_EV and CMP_HP; TAB_COP → DIV_W (y).

The monthly cycle values behind cop.data:

| Month | T_evap (°C) | h1 | h2s | h2 | h3 = h4 (kJ/kg) | COP |
| --- | --- | --- | --- | --- | --- | --- |
| Oct | 10 | 404 | 423 | 427.75 | 256 | 5.28 |
| Nov | 6 | 402 | 423 | 428.25 | 256 | 4.79 |
| Dec | 2 | 399 | 424 | 430.25 | 256 | 4.07 |
| Jan | −2 | 397 | 425 | 432.00 | 256 | 3.67 |
| Feb | 0 | 398 | 424 | 430.50 | 256 | 3.92 |
| Mar | 4 | 400 | 423 | 428.75 | 256 | 4.38 |

The condenser runs at 40 °C (water 38 °C supply, 27 °C return). Efficiencies: isentropic 0.80, mechanical 0.80, belt 0.95, motor 0.96, so W = (h2s − h1)/0.5837 per kg.

R_EV = 0.8605 is the October ratio (h1 − h4)/(h2 − h3) = 148/172. Tables 4.2–4.7 of the thesis use it in every month, so G_EV reproduces those tables. To use each month's own ratio instead, replace G_EV with a product of Q_cond and a fifth table, evap_ratio_monthly.data (0.862 in October to 0.801 in January).

Q_cond never passes the 10 kW capacity: its peak is 9.59 kW, at 06:00 on 16 December 2013.

## Step 4 – Ground heat exchanger check

In the thesis, the ground loop does not change the energy balance: the COP is fixed by month. The loop is checked separately, hour by hour, against the heat the evaporator needs. This step does the same check.

The ground loop is 6 modules × 95 m of ¾" PE pipe (d_i = 21.1 mm) at 1 m depth, with water entering at 2 °C. Eq. (2.24) with the thesis values (L = 90 m in the worked example, F(z) = 1.052554, k_t = 2.42 W/mK) gives the heat it can deliver:

Q_{top} = n\,m\,c_p\,(T_{soil} - T_{s1})\left[1 - e^{-k_t F(z) L/(m c_p)}\right] = 1181.96\,(T_{soil} - 2) \quad \text{at } m = 0.1748 \text{ kg/s}

Q_{top,max} = n\,k_t\,F(z)\,L\,(T_{soil} - 2) = 1375.48\,(T_{soil} - 2) \quad \text{at unlimited flow}

The soil temperature comes from Eq. (2.23), one value per day: T = 17.12 + 13.98·e^(−0.3585)·cos(2π·t*/365 − 0.3585), with t* counted in days from 3 July. It is already in tsoil.data.

| Icon | Component (Signal library) | Setting | Output |
| --- | --- | --- | --- |
| F_GHX | f(x) expression, x = T_soil from TAB_SOIL | 1181.96*(x - 2) | Q_top (W) at design flow |
| F_GMAX | f(x) expression, x = T_soil | 1375.48*(x - 2) | Q_top,max (W) |
| SUB_M | Sum, inputs + Q_top and − Q_evap | – | ground-loop margin (W) |

When the margin is negative, the module flow must rise above 0.1748 kg/s, as in the thesis example: on 3 February at 06:00 the soil is at 7.58 °C, the loop gives 6.60 kW at design flow and needs 0.735 kg/s per module for 7.398 kW. F_GHX gives the same 6.60 kW.

What to expect over the season, with R_EV = 0.8605: the margin is negative in 30 hours (2 in January, 28 in February), when the soil is coldest. In 3 hours (3 February 06:00, 5 February 05:00 and 06:00) Q_evap is even above Q_top,max, so no flow rate is enough. With the monthly ratios of Table 3.7 these numbers fall to 19 hours (all in February) and 0 hours.

## Step 5 – Greenhouse check and energy outputs

A small Thermal network shows that the heat delivered keeps the greenhouse at 18 °C. The thesis neglects the heat stored in the air and the structure; the air node here only makes the check visible.

| Icon | Component (Thermal library) | Value |
| --- | --- | --- |
| T_OUT | Temperature source, signal input from TAB_TOUT | – |
| G_ENV | Thermal conductance | 448.078 W/K (UA_GH) |
| AIR | Thermal capacity | mass 156 kg (air in 130 m³), specific heat 1005 J/(kg·K), initial 18 °C |
| HS_HEAT | Heat flow source, signal input | Q_heat = Q_dir + Q_dis + Q_cond |
| SUM_HEAT | Sum (Signal), inputs + Q_dir, + Q_dis, + Q_cond | Q_heat (W) |

Connections: T_OUT → G_ENV → AIR ← HS_HEAT. When the outdoor air is below 18 °C, Q_heat equals the loss and AIR stays at 18.0 °C. When it is warmer, the thesis demand is zero and AIR floats above 18 °C.

Energy outputs: put an integrator, then a gain of 1/3.6e6, after each power to read kWh.

| Output | Integrated signal | Thesis name |
| --- | --- | --- |
| E_dem | Q_dem | Q_s, greenhouse heat loss |
| E_fay | Q_fay | Q_fay, useful solar heat |
| E_dir | Q_dir | Q_fay-kalan, solar used directly |
| E_ch | Q_ch | Q_dv, heat to the store |
| E_dis | Q_dis | Q_dk, heat from the store |
| E_cond | Q_cond | Q_yoğ, condenser heat |
| E_comp | W | W_k, compressor work |
| E_evap | Q_evap | Q_bi, heat to the evaporator |
| HP_hours | HP_on, then a gain of 1/3600 instead of 1/3.6e6 | heat-pump operating hours |

The seasonal COP is E_cond / E_comp; the solar share is (E_dir + E_dis) / E_dem.

## Simulation settings and expected results

Run a one-day test first, then the whole season.

| Run | Final time | Print interval |
| --- | --- | --- |
| One day, 1 October 2013 | 86 400 s | 600 s |
| Heating season, 1 Oct 2013 – 31 Mar 2014 | 15 724 800 s | 3600 s |

Solver: keep the default variable-step integrator and tolerance, with discontinuity handling on (the relays and comparators switch). All initial values are in the tables above: E = 0 J, AIR = 18 °C.

Season totals to compare with the thesis:

| Output | Thesis | Expected in Amesim |
| --- | --- | --- |
| E_dem, heat demand | 16 748 kWh | 16 748 kWh |
| E_fay, useful solar heat | – | 5 941 kWh |
| E_dir, solar used directly | – | 2 621 kWh |
| E_ch / E_dis, to / from the store | – | 3 320 / 3 307 kWh |
| E_cond, heat-pump heat | 10 820 kWh | 10 821 kWh |
| E_comp, compressor work | 2 626 kWh | 2 626 kWh |
| E_evap, heat from the ground | – | 9 311 kWh |
| HP_hours | 2 265 h | a little below 2 265 h (see note) |
| Peak of E | 150.3 kWh (Section 3.6.1) | 108.5 kWh |
| Seasonal COP | – | 4.12 |

Monthly values (also in expected_monthly_results.csv):

| Month | Demand (kWh) | Solar direct (kWh) | From store (kWh) | Heat pump (kWh) | Compressor (kWh) | COP | HP hours |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Oct 2013 | 1 868 | 221 | 982 | 664 | 126 | 5.28 | 165 |
| Nov 2013 | 2 149 | 280 | 696 | 1 173 | 245 | 4.79 | 308 |
| Dec 2013 | 4 371 | 771 | 149 | 3 451 | 848 | 4.07 | 600 |
| Jan 2014 | 3 015 | 500 | 388 | 2 126 | 579 | 3.67 | 466 |
| Feb 2014 | 2 850 | 477 | 476 | 1 897 | 484 | 3.92 | 377 |
| Mar 2014 | 2 496 | 372 | 615 | 1 509 | 344 | 4.38 | 349 |

Note on HP_hours: the thesis counts every hour in which the heat pump runs at all as one full hour. Amesim counts time continuously, so an hour in which the store empties at 16:40 adds only 20 minutes. The energies are the same; only the hour count comes out slightly lower.

The economics of Section 4.2 (capital cost 21 679 TL, payback after 36, 126 and 158 months against diesel, fuel-oil and coal boilers) follow directly from E_comp and E_dem. They are calculated in the GitHub project, not in Amesim.

## Troubleshooting

| Symptom | Likely cause | Fix |
| --- | --- | --- |
| A table file is refused | Header or separator format of your version | Open the file in the Table Editor and save it again |
| Q_dem at t = 0 is not 4 481 W | Wrong UA_GH or set point, or T_out not from TAB_TOUT | 448.078 W/K and 18 °C |
| E_fay for the season is not 5 941 kWh | Gain is not 7.35, or the table time unit is not seconds | Check G_SOL and the table x unit |
| Results look shifted by one hour | Table time origin | t = 0 s must be 1 Oct 2013, 00:00 |
| E drops far below zero | No lower limit on INT_E and relay thresholds too low | Use a limited integrator, or raise the OFF threshold to 1 J |
| E_cond far above 10 821 kWh | Store discharge not working | Check REL_E output (1 or 0) and MUL_DIS inputs |
| AIR drifts away from 18 °C in cold hours | Sign of HS_HEAT, or Q_heat misses one of its three parts | Q_heat = Q_dir + Q_dis + Q_cond, positive into AIR |
| Very slow run | Many small steps at the 1-second ramps of the tables | Expected with 8 736 ramps; set the print interval to 3600 s and do not tighten the tolerance |
| HP_hours below 2 265 | Continuous counting | Expected; compare energies instead |

## Level B – physical version (beyond the thesis)

Level B keeps every thesis value but replaces the ideal energy counters with water loops, a PCM store with a real temperature and finite heat exchangers. This is the follow-up study the thesis proposes in Chapter 5. Values marked [A] are my assumptions, because the thesis does not need them. Build it only after Level A gives the expected totals.

The layout follows Figure 3.1 of the thesis.

### B1. Setup

- Thermal-Hydraulic library, one fluid properties icon for water (index 1).

- One pressure reference (expansion tank or pressure source, 2 bar abs [A]) in each closed loop.

- Use two mass flow sources with complementary signals (ṁ·S and ṁ·(1 − S)) in place of each three-way valve; they are easier to set up and switch the same way.

### B2. Solar collectors and PCM store

| Icon | Component | Value |
| --- | --- | --- |
| COLL | Chamber with thermal port, plus heat flow source Q_fay = 7.35·I_T on its wall | 12 L [A] |
| P_S | Mass flow source, on while I_T > 0 | 0.6 kg/s, 0.02 kg/s per m² [A] |
| PCM | Thermal capacity with a temperature-dependent specific heat | 3 317 kg (1.94 m³ × 1710 kg/m³); c = 1.4 kJ/(kg·K) below 28 °C, 95 kJ/(kg·K) from 28 to 30 °C (latent heat 187 kJ/kg over 2 K), 2.2 kJ/(kg·K) above 30 °C [A]; initial 20 °C [A] |
| HX_PCM | Chamber in the store + conductance to PCM | 10 L, 500 W/K [A] |

### B3. Greenhouse coil and heat pump

| Icon | Component | Value |
| --- | --- | --- |
| COIL | Chamber (fan-coil water side) + conductance to AIR | 10 L [A], 690 W/K (10 kW at 38/27 °C water and 18 °C air) |
| P_C | Mass flow source, condenser loop | 10 000/(4186 × 11) = 0.217 kg/s |
| COND | Chamber + heat flow source +Q_cond | 3 L [A]; Q_cond and W from Step 3, with COP from cop.data |
| AIR, G_ENV, T_OUT | As in Step 5 | 156 kg, 448.078 W/K |

### B4. Ground loop

| Icon | Component | Value |
| --- | --- | --- |
| P_G | Mass flow source (6 modules in parallel as one loop) | 6 × 0.1748 = 1.049 kg/s |
| GP1…GP5 | Five chambers (or pipe segments) in series, each with a conductance to T_SOIL | 1375.48/5 = 275.1 W/K each |
| T_SOIL | Temperature source, signal input from TAB_SOIL | Eq. (2.23) |
| EVAP | Chamber + heat flow source −Q_evap | 5 L [A] |

Five segments in series reproduce the exponential of Eq. (2.24). Check: with 2 °C water entering and 7.58 °C soil, the loop gives about 6.6 kW, as in the thesis example of 3 February.

### B5. Control and comparison

Keep the thesis order with temperatures instead of energy counters: solar water goes to the coil while AIR is below 18 °C and to the store otherwise; the store is discharged through the coil when AIR is below 18 °C and the PCM is above 25 °C [A]; the heat pump runs when both are not enough (AIR below 17.5 °C [A]).

Run Level A and Level B with the same input files. The differences in E_cond, E_comp and heat-pump hours show the cost of a real store and real heat exchangers. A melting point of 29 °C leaves only about 10 K to heat an 18 °C greenhouse, so expect the store to give back less than in Level A.

## Vocabulary

B2

- threshold – the level at which something switches on or off. "The relay threshold of 1 J keeps E from going below zero."

- margin – the extra amount left over beyond what is needed. "SUB_M … ground-loop margin (W)."

C1

- replica – an exact copy of something. "So the exact replica of the thesis (Level A) is built mostly from Signal blocks."

- negligible – so small that you can ignore it. "E may dip a few joules below zero for one solver step; this is negligible."